## Sheet1
Mark | Description | Manufacturer/Model or General Specification | Comments
1 | P-1-1: ASR Recovery Pump Submersible Pump with integral check valve. | Grundfos Model 150S100-5, 10-HP, 575-Volt/3-P/60Hz, Rated at: 170 gpm@160 ft TDH | Stainless steel pump with integral check valve and submersible motor. Set the pump at ~ 150 ft BLS as shown on Drawing M-2.
2 | FCV-1-2: Downhole Control Valve System | Grundfos 3” Model SPV 50 ATES Submersible Pump Valve system with hydraulic control unit, 240-v/1-P/60 Hz | Provide the required hydraulic hoses and fluid for the valve set at the depth within the well as shown on the Drawings. Coordinate hose fittings with connections through wellhead flange as shown on Drawing M-2.
3 | 3” PVC Drop Pipe: PVC drop pipe connection from submersible pump & downhole control valve to fabricated SST wellhead connections. | CertainTeed Certa-Lok 3” PVC Drop Pipe, ASTM D1785 (Sch 80) system complete with couplings, o-rings, splines, and torque-control set screws | Provide drop pipe as required to set the pump as shown on the Drawings (~150 ft BLS), install the in-line downhole control valve FCV-1-2 (Mark 2 above), and to connect to the fabricated wellhead flange (Mark 5) as shown on Drawing M-2.
4 | 12” Type 316 SST Slip-On Flange | ANSI B16.5 Class 150 Forged Type 316 SST Slip-On Flange | Install true and plumb, bolt holes aligned with fitting to the top of the 12” SST well casing, weld to well casing. Provide rubber gaskets and SST bolt sets as required to connect 12” blind flange (Mark 4) below.
5 | 12” Type 316 SST Blind Flange with Fabricated Modifications | ANSI B16.5 Class 150 Forged Type 316 SST Blind Flange | Modify blind flange with openings and pipe spools as shown Drawing M-2, ASR Wellhead Flange Detail. Utilize qualified fabrication shop and AWS Certified welder.
5a | 3” Type 316L SST Pipe Spool with Fabricated Modifications | 3” ASTM 312 Type 316 SST, Sch 80 pipe with matching ANSI B16.5 slip-on flange welded to the pipe as shown to connect to 3” Certa-Lok drop pipe (Mark 3). | Fabricate pipe spool as shown on Drawing M-2 to connect using Certa-Lok PVC coupling below wellhead flange and flanged connection above. Install through and weld to 12” blind flange as shown.
5b | 1.5” Type 316L SST Pipe Spool for instrument cable pressure seal with fabricated modifications | 1.5” ASTM 312 Type 316 SST, Sch 80 pipe, with NPT top connection for cable pressure seal. | Fabricate pipe spool as shown on Drawing M-2 to connect using 1.5” Poly coupling below wellhead flange for Poly conduit for LE-1-1 submersible level element, and NPT threaded connection for cable pressure seal above. Install through and weld to 12” blind flange as shown.
5c | 1” Type 316L SST Pipe Spool with fabricated modifications | 1 ” ASTM 312 Type 316 SST, Sch 80 pipe, with NPT top connection to air and vacuum relief valve. | Fabricate pipe spool as shown on Drawing M-2 to provide air vent for well casing. Install spool through opening in flange and weld to 12” blind flange as shown. Top of spool to be NPT threaded for connection to AVRV-1-1.
5d | 1.5” Type 316L SST Pipe Spool for power cable pressure seal with fabricated modifications | 1.5” ASTM 312 Type 316 SST, Sch 80 pipe, with NPT top connection for cable pressure seal. | Fabricate pipe spool as shown on Drawing M-2 to route pump power cable through pressure-rated wellhead flange, and NPT threaded connection for cable pressure seal above. Install through and weld to 12” blind flange as shown.
5e | Hydraulic Hose Connections for Downhole Control Valve FCV-1-2 | Grundfos Model SPV 50 ATES Submersible Pump Valve accessories | 0.375” threaded connections for hydraulic control lines to downhole control valve. Confirm requirements with the supplier for the downhole control valve hydraulic hose connections. Drill and install in SST wellhead flange.
5f | Cable Pressure Seal for pump P-1-1 power cable | O-Z Gedney 1.5” Type CSBG conduit sealing bushing | CSBG conduit sealing bushing rated for 50 psi, for sealing submesibel pump power cable to P-1-1. Bronze pressure discs and locking collar, neoprene sealing ring, SST socket head cap screws and washers. Coordinate conduit neoprene sealing ring hole sizes and configuration as required for the power cable as provided.
5g | Cable Pressure Seal for level element LE-1-1 cable | O-Z Gedney 1.5” Type CSBG conduit sealing bushing | CSBG conduit sealing bushing rated for 50 psi, for sealing level element cable to LE-1-1. Bronze pressure discs and locking collar, neoprene sealing ring, SST socket head cap screws and washers. Coordinate conduit neoprene sealing ring hole sizes and configuration as required for the instrument cable as provided.
6 | 3”x3”x3” Flanged PVC Tee | 3"x3"x3" PVC Tee ASTM D2466 and D2467, flanges per ANSI B16.1 | Provide rubber gaskets and SST bolt sets as required.
6a | 3" Type 316 SST Blind Flange with modifications | ANSI B16.5 Class 150 Forged Type 316 SST blind flange | Drill and tap blind flange for 1" NPT type 316 SST pipe nipple for connection to air venting. Top of 1" nipple shall be NPT threaded for connection to AVRV-1-2.Provide rubber gaskets and SST bolt sets as required.
6b | 1” Type 316L SST Pipe Spool (2 required) | 1 ” ASTM 312 Type 316 SST, Sch 80 pipe, with NPT top connection to air and vacuum relief valve. | Fabricated pipe spool with NTP threads to provide air vent for recharge/recovery piping. Connect spool to 1" NTP threaded opening in 3" blind flange. Top of spool to be NPT threaded for connection to AVRV-1-2.
7 | 1" SST Tapping Saddle | Ford Meter Box Style FS313 SST tapping salddle for 3.5" OD (3" Sch 80) PVC pipe | 1" SST tapping salddle for 3.5" OD (3" Sch 80) PVC pipe. Install tapping saddle on 3" PVC piping to provide connection for air venting or pressure transducer.
8 | 3" PVC Piping (Exposed Indoors - Flanged) | 3" Schedule 80 PVC Piping System with PVC solvent welded flanges as shown on Drawing M-1, Schedule 80 PVC, Type I, Grade I, ASTM D1784 and D1785, 125# ANSI B16.1 flanges | Configure flanges to match fittings. As an alternate solvent welded fittings may be used where flanges are not needed for connection to the wellhead, valves, or flow meter. Provide rubber gaskets and SST bolt sets as required.
9 | 3" PVC Piping (Buried Push-On Joint) | 3" AWWA C-900 PVC (ASTM D1784) piping with bell and spigot joints, conforing to ASTM D3139 and elastomeric seals conforming to ASTM F477. | Buried piping to be owner's standard. Provide restrained joints at all buried fittings for connection to flanged or solvent welded PVC system.
10 | 3"x3"x3"x3" Flanged PVC Cross | 3"x3"x3"x3" PVC Cross, ASTM D2466 and D2467, flanges per ANSI B16.1 | Solvent welded fitting with SW flanges may also be used. Adjust dimensions accordingly.
11 | 3" PVC 90° Elbow | 3" PVC 90° Elbow, ASTM D2466 and D2467, flanges per ANSI B16.1 | Solvent welded fitting with SW flanges may also be used. Adjust dimensions accordingly.
12 | 3" PVC Blind Flange | 3" PVC flat-faced flange, 125# ANSI B16.1 flanges | Temporary blind flanges on recovery piping to be replaced in futre by motorized valve.
13 | 3"x2" PVC Reducer | 3" PVC concentric reducer, ASTM D2466 and D2467, flanges per ANSI B16.1 | Reduced diameter control valve connections.
14 | 3" Flanged Motor-Operated Butterfly Valve (open/close service) | 3" Butterfly Valve: Pratt, DeZurk, Mueller, or equal. Motor Operator: Limitorque, Rotork, AUMA or equal. (open/close service) | 3" Butterfly Valve: short-body, AWWA C504, ASTM A126, Class B CI or ASTM A536 DI, 316 SST seat edge, 304 SST shaft, EPDM Seat. Motor Operator: Configured for120 v/1-p/60 Hz, open/close service, position limit indication (discrete signal), local/hand/remote, indicating lights, power supply, reversing starter, manual overide, configured for valve.
15 | 2" Flanged Motor-Operated Butterfly Valve (modulating service) | 3" Butterfly Valve: Pratt, DeZurk, Mueller, or equal. Motor Operator: Limitorque, Rotork, AUMA or equal. (modulating service) | 2" Butterfly Valve: short-body, AWWA C504, ASTM A126, Class B CI or ASTM A536 DI, 316 SST seat edge, 304 SST shaft, EPDM Seat. Motor Operator: Configured for120 v/1-p/60 Hz, modulating service, position indication and signal (4-20 mA output), local/hand/remote, indicating lights, power supply, reversing starterr, manual overide, configured for valve.
16 | 3" Bi-Directional Flowmeter | Seimens MAG5100W, Endress + Hauser Promag, or equal. | Line-sized, 3" flanges, local display (L/s), 4-20 mA output in proportion to flow, flow range: 4 to 20 L/s (63 to 320 gpm), Provide rubber gaskets and SST bolt sets as required.
17 | Pressure Indicating Transmitter | Rosemount Model 3051 TG, SMAR LD301M Series, Foxboro Model IPG10, or equal. | SST pipe nipple connections, Range: 0-100 psi, local indication, 4-20 mA output
18 | Pressure Gauge | Ashcroft, Dwyer, or equal. | SST pipe nipple connections, Range: 0-100 psi, 2.5" dial
19 | Submersible Level Element | Druk Type PDCR 35/D with SCU 220, Endress + Hauser Model FMX167, or equal. | Loop-powered, Range: 0 to 200 psi, 4-20 mA output